## Notes
Questions and Action Items
Final revisions from community feedback
| 15 vs. 10 min intervals | Added History Interval term defining 10 minutes as new building standard. Retrofit work should conform to any existing standard. Intervals should be consistent on all points on a piece of equipment.
| Changed noHC to noHeat, noCC to noCool more consistent with heat and cool tag | The existence of the "no" tag ensures there was no oversight in the heating/cooling method being left off. Not intended to find equipment without a particular feature.
| Primary & Secondary | Primary and Secondary tags will always be used in the context of the site. Primary indicates equipment or points related to sources coming to (campus distribution) or created within the site (building/central/district plant) Secondary indicates equipment or points related to distribution throughout the site (campus or building areas)
| Mixed Air Damper | Added point and term definition
| Cmd vs. Pos | The naming convention Cmd vs. Pos for Boolean vs. Numeric valves and dampers is mainly for convenience in importing into analytics to correctly assign the data type and unit. Pos is a very common naming convention for modulated valves and dampers.
| DHW Supply/Return vs. Leaving/Entering | CHWS, HWS and DHW Tags changed from supply to leaving, return to entering
| humidify vs. deHumidify Setpoint | For systems that humidify and dehumidify it is common to have two different setpoints.
| All other suggestions updated in the document | Additional points, minor tag cleanup

## Terms
Standard Terms
Term | Definition
Circulation (Pump) | A pump within the plant that circulates a fluid through an individual piece of equipment such as a chiller, boiler, cooling tower or heat exchanger.
Command | Indicates a piece of equipment, valve, damper or fan has been command to a Boolean value of on/off or open/close. (See Enabled, Status and Position for related points)
Effective | Indicates the current temperature or pressure setpoint target given the current mode of operation. For a temperature or flow set point this value would change as a piece of equipment moves between occupied and unoccupied and heating and cooling modes.
Enabled | A Boolean software point indicating a piece of equipment is in or out of service and is available or not available to be commanded on or off. It does not indicate a piece of equipment is running or not running. Enabled should never be used to indicate the commanding of a point or piece of equipment on or off. Commonly used to take a piece of equipment out of service for maintenance or repair. Control logic will ignore equipment that is not enabled. (See Command and Status for related points)
Energy | Tracks the consumption of a unit of energy (kWh, MMbtu, etc.). Always an accumulated value with a hisTotalized tag.
Exhaust | Indicates undesired air leaving the building due to contaminants or other undesirable components like excess heat or humidity. Common areas would include mechanical areas, dryers, pools and laboratories.
History Intervals | Numeric history intervals for new projects with newer controlers and adequate memory should be 10 minutes. Retrofit work should coorespond with the existing intervals. In all cases the history interval should be the same for all points on a piece of equipment so that histories align on the same time boundareis.
Frequency | Frequency is a numeric value either commanding or sensing a VFD running at a specific Hz. See Speed for VFD percent control.
Loop (Pump) | A pump that distributes a fluid to a larger area such as a campus, district or building for end equipment use.
Mixed Air Damper | Mixed air damper should only be used when there is a specific third damper controlling mixed air separate from the the outside air damper and the return air damper. A two damper configuration of outside and return air dampers should never name one of the dampers as a mixed air damper.
Mode | A software point indicating the current operating intent of a piece of equipment. Used to understand the current system mode (i.e. Occupancy, Dehumidifing, Economizing, IAQ, etc.) when analyzing related points.
Occupancy | A Boolean point indicating a unit is in occupied or unoccupied mode.
Phase | Indicates electrical attributes (amps, volts, power or energy) as measured across an individual phase. A string value containing A, B, C, AB, BC, AC, AN, BN, CN.
Power | Tracks the instantaneous value of power (kW, MMbtu/h, etc.).
Position | A numeric value indicating a valve or damper open position between 0 and 100%.
PreHeat | Preheat indicates heating coils and valves intended to heat outside air to prevent the freezing of cooling coils. Often seen in cold climates with minimum outside air damper positions or large outside air requirements.
Primary | The primary tag is always used in the context of the site. Primary refers to piping, valves, pumps and sensors within the central plant that moves water between equipment in the plant. Common primary equipment includes individual chillers, boilers, heat exchangers, isolation valves, pumps and sensors.
Relief | Indicates excess air leaving the building in order to maintain overall building static pressure and indoor air quality.
Room | This term should not be used. Use "Zone" instead.
Secondary | The secondary tag is always used in the context of the site. Secondary refers to equipment or points moving air or fluids away from a source to another area for use. Common sources may include chilled water or hot water plants within a building or a central or district plant on a campus. Common uses may include campus distribution of chilled water, hot water, or steam; or chilled, hot or domestic water loops within a building.
Space | This term should not be used. Use "Zone" instead.
Speed | A numeric value commanding a fan or pump to run at a percentage of capacity from 0 to 100 percent.
Status | A Boolean point indicating proof a commanded action happened. Typically based on a measure of flow (air, water, current) resulting from the commanded action. Status should never be used to indicate the commanding of a point on or off. (See Command and Enabled for related points)
Zone | Zone is the general term used to define any area served by a VAV, FCU or direct zone AHU. The term “Room” or "Space" should not be used.
Total | Indicates the total power or energy across all phases of electricity.

## Abbreviations
Standard Abbreviations
Term | Abbreviation
Building Loop Pumps | P
Carbon Dioxide | CO2
Chilled Water | ChW
Chilled Water System | CHWS
Command | Cmd
Condenser Water | CW
Circulation Pump (individual equipment) | CP
Damper | Dmpr
Domestic Hot Water System | DHW
Enable | Enab
Entering | E
Frequency | Freq
Heat Exchanger | Hx
Hot Water | HW
Hot Water System | HWS
Leaving | L
Load | Load
Mechanical | Mech
Mixing | Mix
Occupancy/Occupied | Occ
Position | Pos
Power Factor | PF
Pre-Heat | PreHeat
Pressure | Press
Primary | Pri
Re-Heat | ReHeat
Setpoint | Sp
Speed | Spd
Static Pressure | Press
Status | Sts
Temperature | Temp
Valve | Vlv
Variable Frequency Drive | VFD
UnOccupied | Unocc
Water | Wtr

## AirSide Systems
Airside Equipment | AHU With Return Air | equip, hvac, ahu, [rtu], [elecHeat, hotWaterHeat, steamHeat, gasHeat, noHeat], [chilledWaterCool, dxCool, noCool], [directZone, vavZone, chilledBeamZone, multiZone], [singleDuct, dualDuct, tripleDuct], [hotDeck, coldDeck, neutralDeck], [constantVolume, variableVolume] [humidifier, noHumidifier], hotWaterPlantRef, chilledWaterPlantRef (plant?)
| AHU with Makeup Air | equip, hvac, ahu, mau
| FCU | equip, hvac, fcu, [elecHeat, hotWaterHeat, noHeat] [chilledWaterCool, noCool]
Description | Control Point Name (navName) | Tags | Point Type | UoM | History | Haystack Tags | Haystack Compliance Notes
General Points
Occupied Mode | Occ | occupied, cmd | Bool | Occ/UnOcc | COV, 24hr | - | -
Building Static Pressure | BldgPress | building, air, pressure, sensor | Num, .01 | in w.c. | Int, 10 min | zone, air, pressure, sensor | building is not a haystack tag for points
Building Static Pressure Setpoint | BldgPressSp | building, air, pressure, sp | Num, .01 | in w.c. | COV, 24hr | zone, air, pressure, sensor | building is not a haystack tag for points
Filters
Filter Status | FilterSts | filter, run, sensor | Bool | Ok/Dirty | COV, 24hr
Filter Pressure Delta | FilterPressDelta | filter, pressure, delta, sensor | Num, .01 | in w.c. | Int, 10 min | - | -
PreFilter Pressure Delta | PreFilterPressDelta | filter, pressure, delta, sensor | Num, 1 | ∆ in w.c. | Int, 10min | - | New point still needs compared to Haystack
FinalFilter Pressure Delta | FinalFilterPressDelta | filter, pressure, delta, sensor, final | Num, 1 | ∆ in w.c. | Int, 10min | - | New point still needs compared to Haystack
Single Direct Zone Points
Zone CO2 | ZoneCO2 | zone, co2, sensor | Num, 0 | ppm | Int, 10min | zone, air, co2, sensor
Zone CO2 Setpoint | ZoneCO2Sp | zone, co2, sp, hisMode:cov | Num, 0 | ppm | COV, 24hr | zone, air, co2, sp
Zone Pressure | ZonePress | zone, air, pressure, sensor | Num, .01 | in w.c. | Int, 10min | - | -
Zone Pressure Setpoint | ZonePressSp | zone, air, pressure, sp, hisMode:cov | Num, .01 | in w.c. | COV, 24hr | - | -
Zone Temperature | ZoneTemp | zone, air, temp, sensor | Num, 1 | F | Int, 10min | - | -
Zone Temperature Setpoint (effective) | ZoneTempSp | zone, air, temp, effective, sp | Num, 0 | F | Int, 10min | - | -
Occupied Cooling Setpoint | OccCoolSp | occ, cooling, zone, air, temp, sp, hisMode:cov | Num, 0 | F | COV, 24hr | - | -
Occupied Heating Setpoint | OccHeatSp | occ, heating, zone, air, temp, sp, hisMode:cov | Num, 0 | F | COV, 24hr | - | -
Unoccupied Cooling Setpoint | UnoccCoolSp | unocc, cooling, zone, air, temp, sp, hisMode:cov | Num, 0 | F | COV, 24hr | - | -
Unoccupied Heating Setpoint | UnoccHeatSp | unocc, heating, zone, air, temp, sp, hisMode:cov | Num, 0 | F | COV, 24hr | - | -
Discharge Air Points - VAV Zones
DA Fan Command (single or common) | DaFanCmd | discharge, air, fan, run, cmd | Bool | On/Off | COV, 24hr | - | -
DA Fan Status (single or common) | DaFanSts | discharge, air, fan, run, sensor | Bool | On/Off | COV, 24hr | - | -
DA Fan Speed (single or common) | DaFanSpd | discharge, air, fan, speed, cmd | Num, 0 | % | Int, 10min | - | -
DA Fan Frequency (single or common) | DaFanFreq | discharge, air, fan, freq, sensor | Num, 0 | Hz | Int, 10min | - | -
DA Air Flow | DaFlow | discharge, air, flow, sensor | Num, 1 | cfm | Int, 10min | - | New point still needs compared to Haystack
DA Humidity | DaHumidity | discharge, air, humidity, sensor | Num, 0 | % | Int, 10min | - | -
DA Pressure | DaPress | discharge, air, pressure, sensor | Num, .01 | in w.c. | Int, 10min | - | -
DA Pressure Setpoint | DaPressSp | discharge, air, pressure, sp, hisMode: cov | Num, .01 | in w.c. | Int, 10min | - | -
DA Temp | DaTemp | discharge, air, temp, sensor | Num, 1 | F | Int, 10min | - | -
DA Temp Setpoint | DaTempSp | discharge, air, temp, sp, hisMode:cov | Num, 0 | F | COV, 24hr | - | -
Systems with Return Air
RA CO2 | RaCO2 | return, co2, sensor | Num, 0 | ppm | Int, 10min | return, air, co2, sensor | air tag is needed for all points associated with the measurement or control of air
RA CO2 Setpoint | RaCO2Sp | return, co2, sp, hisMode:cov | Num, 0 | ppm | COV, 24hr | return, air, co2, sp | air tag is needed for all points associated with the measurement or control of air
RA Damper Position | RaDmprPos | return, air, damper, cmd, outside, | Num, 0 | % | Int, 10min | return, air, damper, sensor | "outside" tag is associated with outside air, a position point typically is a feedback
RA DeHumidify Setpoint | RaDehumidSp | return, air, humidity, deHumidify, sp, hisMode:cov | Num, 0 | %RH | COV, 24hr | return, air, dehumid, sp, hisMode:cov | deHumidify and dehumid are both not defined tags in Haystack 3.0, but "dehumid" should be more aligned with Haystack 4.0
RA Humidify Setpoint | RaHumidSp | return, air, humidity, humidify, sp, hisMode:cov | Num, 0 | %RH | COV, 24hr | - | -
RA Humidity | RaHumidity | return, air, humidity, sensor | Num, 0 | %RH | Int, 10 min | - | -
RA Flow | RaFlow | return, air, flow, sensor | Num, 1 | cfm | Int, 10min | - | -
RA Fan Command (single or common) | RaFanCmd | return, air, fan, run, cmd | Bool | On/Off | COV, 24hr | - | New point still needs compared to Haystack
RA Fan Status (single or common) | RaFanSts | return, air, fan, run, sensor | Bool | On/Off | COV, 24hr | - | -
RA Fan Speed (single or common) | RaFanSpd | return, air, fan, speed, cmd | Num, 0 | % | Int, 10 min | - | -
RA Fan Frequency (single or common) | RaFanFreq | return, air, fan, freq, sensor | Num, 0 | Hz | Int, 10min | - | -
RA Pressure | RaPress | return, air, pressure, sensor | Num, .01 | in w.c. | Int, 10min | - | -
RA Pressure Setpoint | RaPressSp | return, air, pressure, sp | Num, .01 | in w.c. | COV, 1hr | - | -
RA Temp | RaTemp | return, air, temp, sensor | Num, 1 | F | Int, 10min | - | -
Return Air Damper Command | RaDmprCmd | return, air, damper, cmd | Num, 1 | % | Int, 10min | - | New point still needs compared to Haystack
Systems with Relief Air
Relief Air Damper Position | RlfDmprPos | relief, air, damper, cmd | Num, 0 | % | Int, 10 min | - | -
Systems with Outside Air
Outside Air Damper Command (open/closed) | OaDmprCmd | outside, air, damper, cmd | Bool | Open/Closed | COV, 24hr | - | -
Outside Air Damper Position | OaDmprPos | outside, air, damper, cmd | Num, 0 | % | Int, 10 min | outside, air, damper, sensor | Position points are typically not commands
Outside Air Flow | OaFlow | outside, air, flow, sensor | Num, 0 | cfm | Int, 10 min | - | -
Outside Air Humidity | OaHumidity | outside, air, humidity, sensor | Num, 0 | %RH | Int, 10 min | - | -
Outside Air Temperature | OaTemp | outside, air, temp, sensor | Num, 1 | F | Int, 10 min | - | -
Mixed Air Points
Mixed Air Temp | MaTemp | mixed, air, temp, sensor | Num, 1 | F | Int, 10min | - | -
Mixed Air Damper Position | MaDmprPos | mixed, air, damper, cmd | Num, 0 | % | Int, 10min | mixed, air, damper, sensor | Position points are typically not commands
Systems with Heating
Heating Water Circulation Pump Command | HWCPCmd | hot, water circ, pump, run, cmd | Bool | On/Off | COV, 24hr
Heating Water Circulation Pump Status | HWCPSts | hot, water circ, pump, run, sensor | Bool | On/Off | COV, 24hr
Heating Water Coil Air Leaving Temp | HCALTemp | heat, air, temp, leaving, sensor | Num, 1 | F | Int, 10min | heat, hot, sensor, valve, water | "heat" tag is associated with hot water valves, position points are typically not commands
Heating Water Coil Valve Command | HWVlvCmd | hot, water, valve, cmd | Num, 0 | % | Int, 10min | sensor, hot, preheat, valve, water | "preheat" is more aligned with Haystack 4.0 syntax , position points are typically not commands
Preheat Coil Valve Command | PreheatVlvCmd | preHeat, water, valve, cmd | Num, 0 | % | Int, 10min | air, heatingCoil, leaving, sensor, temp | heatingCoil is defined in Haystack 4.0
Preheat Coil Air Leaving Temp | PreHCALTemp | preHeat, air, temp, leaving, sensor | Num, 1 | F | Int, 10min | air, preheatCoil, leaving, sensor, temp | "preheatCoil" is more aligned with Haystack 4.0 syntax
Systems with Cooling
Chilled Water Pump Command | ChWCPCmd | chilled, water, pump, run, cmd | Bool | On/Off | COV, 24hr | - | -
Chilled Water Pump Status | ChWCPSts | chilled, water, pump, run, sensor | Bool | On/Off | COV, 24hr | - | -
Chilled Water Valve Command | ChWVlvCmd | chilled, water, valve, cmd | Num, 0 | % | Int, 10min | chilled, water, valve, cmd, cool | "cool" tag is associated with ahu cooling coil
Chiller Water Temp Entering | CHWEtemp | chilled, water, temp, entering, sensor | Num, 1 | F | Int, 10min | - | -
Chiller Water Temp Leaving | CHWLtemp | chilled, water, temp, leaving, sensor | Num, 1 | F | Int, 10min | - | -
Chilled Water Flow | CHWFlow | chilled, water, flow, sensor | Num, 0 | gpm | Int, 10min | - | -
Cooling Coil Air Leaving Temp | CCALTemp | cool, air, temp, leaving, sensor | Num, 1 | F | Int, 10min | air, coolingCoil, leaving, temp, sensor | coolingCoil is defined in Haystack 4.0
Cooling Coil Air Leaving Humidity | CCALHumidity | cool, air, humidity, leaving, sensor | Num, 1 | F | Int, 10min | air, coolingCoil, leaving, humidity, sensor | coolingCoil is defined in Haystack 4.0
DX Cooling Command | DxCoolCmd | cmd,compressor,cool,run | Bool | On/Off | COV, 24hr | - | New point still needs compared to Haystack
DX Cooling Status | DxCoolSts | compressor,cool,run,sensor | Bool | On/Off | COV, 24hr | - | New point still needs compared to Haystack
Dx Coil Air Leaving Temp | DxCALTemp | coilDirectExpansion, air, temp, leaving, sensor | Num, 1 | F | Int, 10min | - | New point still needs compared to Haystack
Systems that Economize
Economize Mode | EconomizeMode | economize, run, cmd | Bool | Active/Inactive | COV
Systems that Humidify
Humidifier Enable | HumidifierEnab | humidifier, enable, cmd | Bool | Enabled/Disabled | COV | - | -
Humidifier Command | HumidifyCMD | humidifier, run, cmd | Bool | On/Off | COV | - | -
See Return Air Humidity & Humidify Setpoint | [5 empty] | - | -
Systems with Direct Evaporative Cooling
Direct Evaporative System Pump Start/Stop | DirEvapPumpSS | cmd,cool,directEvap,pump,run,water | Bool | Start/Stop | COV, 24hr | - | New point still needs compared to Haystack
Direct Evaporative System Pump Status | DirEvapPumpSts | cool,directEvap,pump,run,sensor,water | Bool | On/Off | COV, 24hr | - | New point still needs compared to Haystack
Direct Evaporative System Fill Valve Command | DirEvapFillVlvCmd | directEvap,valve,fill,cmd | Num, 1 | % | Int, 10min | - | New point still needs compared to Haystack
Direct Evaporative System Drain Valve Command | DirEvapDrnVlvCmd | directEvap,valve,drain,cmd | Num, 1 | % | Int, 10min | - | New point still needs compared to Haystack
Direct Evaporative System Makeup Water Flow | DirEvapMWFlow | directEvap,makeup,water,flow,sensor | Num, 1 | gal/min | Int, 10min | - | New point still needs compared to Haystack
Direct Evaporative System Makeup Water Usage | DirEvapMWUsage | directEvap,makeup,water,volume,sensor | Num, 1 | gal | Int, 10min | - | New point still needs compared to Haystack
Systems with Indirect Evaporative Cooling
Indirect Cooling Water Coil Valve Command | ICLGWVlvCmd | indirectEvap, water, valve, cmd | Num, 0 | % | Int, 10min | - | New point still needs compared to Haystack
Indirect Cooling Water Coil Air Leaving Temp | ICLGWCALTemp | heat, air, temp, leaving, sensor | Num, 1 | F | Int, 10min | - | New point still needs compared to Haystack
Systems that Dehumidify
DeHumidify Mode | DeHumidifyMode | deHumidify, run, cmd | Bool | Active/Inactive | COV | dehumid, run, cmd | deHumidify and dehumid are both not defined tags in Haystack 3.0, but "dehumid" should be more aligned with Haystack 4.0
See Return Air Humidity & Dehumidify Setpoint | [5 empty] | - | -
Energy Points - Heat Recovery Water |  | equip, water, meter, hru
Heat Recovery Water Temp Entering | HRUWEtemp | water, temp, entering, sensor | Num, 1 | F | Int, 10min | water, temp, entering, sensor, heatRecovery | Are these points going to be nested underneat an AHU, or are they going to be broken into separate equipment?
Heat Recovery Water Temp Leaving | HRUWLTemp | water, temp, leaving, sensor | Num, 1 | F | Int, 10min | water, temp, leaving, sensor,heatRecovery | Are these points going to be nested underneat an AHU, or are they going to be broken into separate equipment?
Heat Recovery Water Volumertic Flow | HRUWFlow | water, flow, sensor | Num, 1 | gal/min | Int, 10min | water, flow, sensor, heatRecovery | Are these points going to be nested underneat an AHU, or are they going to be broken into separate equipment?
Heat Recovery Water Energy (accumulated) | HRUWEnergy | water, energy, hisTotalized, sensor | Num, 0 | MMbtu | Int, 10min | water, energy, hisTotalized, sensor, heatRecovery | Are these points going to be nested underneat an AHU, or are they going to be broken into separate equipment?
Heat Recovery Water Power | HRUWPower | water, power, sensor | Num, 0 | MMbtu/h | Int, 10min | water, power, sensor, heatRecovery | Are these points going to be nested underneat an AHU, or are they going to be broken into separate equipment?
Heat Recovery Pump Command | HRUCPCmd | hru, circ, pump, run, cmd | Bool | On/Off | COV, 24hr | heatRecovery, circ, pump, run, cmd | Are these points going to be nested underneat an AHU, or are they going to be broken into separate equipment?
Heat Recovery Air Leaving Temp | HRUALTemp | hru, air, temp, leaving, sensor | Num, 1 | F | Int, 10min | heatRecovery, air, temp, leaving, sensor | Are these points going to be nested underneat an AHU, or are they going to be broken into separate equipment?
Fan Coil Systems
Zone Discharge FCU flow | ZoneDaFlow | discharge, air, flow, sensor | Num, 1 | cfm | Int, 10min | - | New point still needs compared to Haystack
Fan Command | FanCmd | fan, run, cmd | Bool | On/Off | COV, 24hr | discharge, fan, air, run, cmd | Only fan a fcu has is a discharge fan
Fan Status | FanSts | fan, run, sensor | Bool | On/Off | COV, 24hr | discharge, fan, air, speed, cmd | Only fan a fcu has is a discharge fan
Fan Speed | FanSpeed | fan, speed, cmd | enum | Off/Low/Med/High | COV, 24hr | discharge, fan, speed, cmd | Only fan a fcu has is a discharge fan
While the four occ/unocc heating/cooling setpoints above rarely change, their histories are needed in analytics to determine when temperatures have drifted too high or low.

## Terminal Units
Terminal Units |  | equip, vav, ahuRef, [fanPowered, series, parallel], [singleDuct, dualDuct], [hotWaterReheat, elecReheat, coolOnly]
Description | Point Name navName | Tags | Point Type | UoM | History | Haystack Tags | Haystack Compliance Notes
Occupied Mode | Occ | occupied, cmd | Bool | Occ/UnOcc | COV, 24Hr | - | -
Discharge Air Flow | DaFlow | discharge, air, flow, sensor | Num, 0 | cfm | Int, 10min | - | -
Discharge Air Flow Setpoint | DaFlowSp | discharge, air, flow, effective, sp | Num, 0 | cfm | Int, 10min | - | -
Damper Position | DmprPos | air, damper, cmd | Num, 0 | % | Int, 10min | air, damper, discharge, sensor | Position points typically are not commands
Reheat Valve | HWVlvlPos | reheat, water, valve, cmd | Num, 0 | % | Int, 10min | hot, reheat, water, valve, sensor | Position points typically are not commands
Discharge Air Temperature | DaTemp | discharge, air, temp, sensor | Num, 1 | F | Int, 10min | - | -
Zone Temperature | ZoneTemp | zone, air, temp, sensor | Num, 1 | F | Int, 10min | - | -
Zone Temperature Setpoint (effective) | ZoneTempSp | zone, air, temp, effective, sp | Num, 0 | F | COV, 24Hr | - | -
Occupied Cooling Setpoint | OccCoolSp | occ, cooling, zone, air, temp, sp, hisMode:cov | Num, 0 | F | COV, 24hr | - | -
Occupied Heating Setpoint | OccHeatSp | occ, heating, zone, air, temp, sp, hisMode:cov | Num, 0 | F | COV, 24hr | - | -
Unoccupied Cooling Setpoint | UnoccCoolSp | unocc, cooling, zone, air, temp, sp, hisMode:cov | Num, 0 | F | COV, 24hr | - | -
Unoccupied Heating Setpoint | UnoccHeatSp | unocc, heating, zone, air, temp, sp, hisMode:cov | Num, 0 | F | COV, 24hr | - | -
Zone Humidity | ZoneHumidity | zone, air, humidity, sensor | Num, 0 | %RH | Int, 10min | - | -
Zone Humidity Setpoint | ZoneHumiditySp | zone, air, humidity, sp | Num, 0 | %RH | Int, 10min | - | -
Zone CO2 | ZoneCO2 | zone, air, co2, sensor | Num, 0 | ppm | Int, 10min | - | -
Zone CO2 Setpoint | ZoneCO2Sp | zone, air, co2, sp | Num, 0 | ppm | Int, 10min | - | -
Optional Commissioning Points
Cooling Max Flow | CoolMaxFlow | cooling, max, flow, sp | Num, 0 | cfm | COV, 24hr | discharge, air, flow, max, cooling, sp
Cooling Min Flow | CoolMinFlow | cooling, min, flow, sp | Num, 0 | cfm | COV, 24hr | discharge, air, flow, min, cooling, sp
Heating Max Flow | HeatMaxFlow | heating, max, flow, sp | Num, 0 | cfm | COV, 24hr | discharge, air, flow, max, heating, sp
Heating Min Flow | HeatMinFlow | heating, min, flow, sp | Num, 0 | cfm | COV, 24hr | discharge, air, flow, min, heating, sp
Fan Powered Boxes
Fan Speed | FanSpeed | fan, speed, run, cmd | Num, 0 | % | Int, 10min | - | -
Fan High Speed | FanSpeedHigh | fan, speed, high, run, cmd | Bool | On/Off | COV, 24Hr | - | -
Fan Medium Speed | FanSpeedMed | fan, speed, med, run, cmd | Bool | On/Off | COV, 24Hr | - | -
Fan Low Speed | FanSpeedLow | fan, speed, low, run, cmd | Bool | On/Off | COV, 24Hr | - | -

## CHW System
Chiller |  | equip, chiller, chilledWaterPlantRef, [absorption, reciprocal, screw, centrifugal], [waterCooled, airCooled]
Description | Point Name navName | Tags | Point Type | UoM | History | Haystack Tags | Haystack Compliance Notes
Chiller Enable | ChrEnab | chiller, enable, cmd | Bool | Enabled/Disabled | COV, 24hr | enable, cmd | "chiller" is only an equip level tag in Haystack
Chiller Command | ChrCmd | chiller, run, cmd | Bool | On/Off | COV, 24hr | run, cmd | "chiller" is only an equip level tag in Haystack
Chiller Status | ChrSts | chiller, run, sensor | Bool | On/Off | COV, 24hr | run, sensor | "chiller" is only an equip level tag in Haystack
Condenser Water Isolation Valve | CWVlvCmd | condenser, isolation, valve, cmd | Bool | Open/Closed | COV, 24hr | - | -
Condesner Water Circulation Pump | CWCPCmd | condenser, circ, pump, cmd | Bool | On/Off | COV, 24hr | - | -
Condenser Water Entering Temperature | CWETemp | condenser, water, entering, temp, sensor | Num, 1 | F | Int, 10min | - | -
Condenser Water Leaving Temperature | CWLTemp | condenser, water, leaving, temp, sensor | Num, 1 | F | Int, 10min | - | -
Chilled Water Isolation Valve | ChWVlvCmd | chilled, isolation, valve, cmd | Bool | Open/Closed | COV, 24hr
Chilled Water Entering Temperature | ChWETemp | chilled, water, entering, temp, sensor | Num, 1 | F | Int, 10min | - | -
Chilled Water Leaving Temperature | ChWLTemp | chilled, water, leaving, temp, sensor | Num, 1 | F | Int, 10min | - | -
Chilled Water Setpoint | ChWSp | chilled, water, leaving, temp, sp, hisMode:cov | Num, 0 | F | COV, 24hr | - | -
Chilled Water Flow | ChWFlow | chilled, water, flow, sensor | Num, 0 | gal/min | Int, 10min | - | -
Oil Temp | ChrOilTemp | oil, temp, sensor | Num, 1 | F | Int, 10min | - | -
Oil Heater Command | ChrOilHeatCmd | oil, heater, run, cmd | Bool | On/Off | COV, 24hr | - | -
Oil Heater Status | ChrOilHeatSts | oil, heater, run, sensor | Bool | On/Off | COV, 24hr | - | -
Load | ChrLoad | load, sensor | Num, 0 | % | Int, 10min | - | -
Energy Points - Electric |  | equip, elec, meter, chiller
Tons | ChrTons | chilled, water, power, sensor | Num, 0 | tonref | 5 COV, 1hr | - | -
Current | ChrCurrent | mag, current, sensor | Num, 0 | A | 5 COV, 1hr | - | -
Volts | ChrVolts | volt, mag, sensor | Num, 0 | V | 5 COV, 1hr | - | -
Energy Total (accumulated) | ChrEnergy | elec, energy, total, sensor, hisTotalized | Num, 0 | kWh | Int, 10min | - | -
Power Total | ChrPower | elec, power, total, active, sensor | Num, 0 | kW | Int, 10min | - | -
Power Factor Total | ChrPF | pf, total, sensor | Num, 0.01 | unitless | Int, 10min | - | -
Energy Points - Water |  | equip, water, meter, chiller
Chilled Water Volume (accumulated) | ChWVolume | water, volume, total, sensor | Num, 0 | gal | Int, 10min | - | -
Chilled Water Energy (accumulated) | ChWEnergy | water, energy, hisTotalized, sensor | Num, 0 | btu | Int, 10min | - | -
Chilled Water Power | ChWPower | water, power, sensor | Num, 0 | btu/h | Int, 10min | - | -
CHWS (Chilled Water System) |  | equip, chilledWaterPlant
Description | Point Name navName | Tags | Point Type | UoM | History
Chilled Water Supply Temp | ChWSTemp | chilled, water, leaving, temp, sensor | Num, 1 | F | Int, 10min
Chilled Water Supply Temp Setpoint | ChWSTempSp | chilled, water, leaving, temp, sp | Num, 0 | F | COV, 24 hr
Chilled Water Return Temp | ChWRTemp | chilled, water, entering, temp, sensor | Num, 1 | F | Int, 10min
Chilled Water Pressure Delta | ChWPressDelta | chilled, water, pressure, delta, sensor | Num, 0 | psi | Int, 10 min
Chilled Water Pressure Delta Setpoint | ChWPressDeltaSp | chilled, water, pressure, delta, sp | Num, 0 | psi | COV, 24 hr
Chilled Water Building Loop Pumps |  | equip, chilled, water, pump, secondary
Building Loop Pump Enable | ChWPEnab | chilled, water, pump, enable, cmd | Bool | Enabled/Disabled | COV, 24hr | - | -
Building Loop Pump Command | ChWPCmd | chilled, water, pump, run, cmd | Bool | On/Off | COV, 24hr | - | -
Building Loop Pump Status | ChWPSts | chilled, water, pump, run, sensor | Bool | On/Off | COV, 24hr | - | -
Building Loop Pump VFD Speed | ChWPVFDSpd | chilled, water, pump, speed, cmd | Num, 0 | % | Int, 10min | - | -
Building Loop Pump VFD Frequency | ChWPVFDFreq | chilled, water, pump, freq, sensor | Num, 0 | Hz | Int, 10min | - | -
Building Loop Return Valve Command | ChWRetVlvCmd | chilled, water, return, isolation, valve, cmd | Bool | Open/Closed | COV, 24hr | - | -
Building Loop Return Valve Sensor | ChWRetVlvSts | chilled, water, return, valve, sensor | Bool | On/Off | COV, 24hr | - | -
Energy Points - Electric |  | equip, elec, meter, chilled, water, pump, [siteMeter, submeterOf]
VFD Energy Total (accumulated) | ChWPVFDEnergy | chilled, water, pump, elec, energy, total, sensor, hisTotalized | Num, 0 | kWh | Int, 10min
VFD Power Total | ChWPVFDPower | chilled, water, pump, elec, power, total, active, sensor | Num, 0 | kW | Int, 10min
Chilled Water Heat Exchanger |  | equip, chilled, water, heatExchanger
Chilled Water Heat Exchanger Enabled | HxChWEnab | enable, cmd | Bool | Enabled/Disabled | COV, 24hr
Chilled Water Heat Exchanger Command | HxChWCmd | run, cmd | Bool | On/Off | COV, 24hr
Chilled Water Heat Exchanger Runtime | HxChWRuntime | chilled, water, total, sensor | Num, 1 | h | Int, 10min
HX Chilled Water Entering Temperature | HxChWETemp | chilled, water, entering, temp | Num, 1 | F | Int, 10min
HX Chilled Water Leaving Temperature | HxChWLTemp | chilled, water, leaving, temp | Num, 1 | F | Int, 10min
HX Chilled Water Isolation Valve | HxChWVlvCmd | chilled, water, isolation, valve, cmd | Bool | Open/Closed | COV, 24hr
HX Chilled Water Circulation Pump Command | HxChWCPCmd | chilled, water, circ, pump, run, cmd | Bool | On/Off | COV, 24hr
HX Chilled Water Circulation Pump Status | HxChWCPSts | chilled, water, circ, pump, run, sensor | Bool | On/Off | COV, 24hr
HX Condenser Water Entering Temperature | HxCWETemp | condenser, entering, water, temp | Num, 1 | F | Int, 10min
HX Condenser Water Leaving Temperature | HxCWLTemp | condenser, leaving, water, temp | Num, 1 | F | Int, 10min
HX Condenser Water Isolation Valve | HxCWVlvCmd | condenser, isolation, valve, cmd | Bool | Open/Closed | COV, 24hr
Condenser Circ Pump Command | HxCWCPCmd | condenser, water, circ, pump, cmd | Bool | On/Off | COV, 24hr
Condenser Circ Pump Status | HxCWCPSts | condenser, water, circ, pump, sensor | Bool | On/Off | COV, 24hr
Cooling Tower |  | equip, coolingTower [openLoop, closedLoop]
Description | Point Name navName | Tags | Point Type | UoM | History
Cooling Tower Enabled | CTEnab | enable, cmd | Bool | Enabled/Disabled | COV, 24
CT Condenser Water Entering Temperature | CTCWETemp | condenser, water, entering, temp, sensor | Num, 1 | F | Int, 10min
CT Condenser Water Leaving Temperature | CTCWLTemp | condenser, water, leaving, temp sensor | Num, 1 | F | Int, 10min
Sump Temperature | CTSumpTemp | sump, temp, sensor | Num, 1 | F | Int, 10min
Sump Heater Command | CTSumpHtrCmd | sump, heating, run, cmd | Bool | On/Off | COV, 24
Sump Heater Status | CTSumpHtrSts | sump, heating, run, sensor | Bool | On/Off | COV, 24
Fan Enabled | CTFanEnab | fan, enable, cmd | Bool | Enabled/Disabled | COV, 24
Fan Command | CTFanCmd | ran, run, cmd | Bool | On/Off | COV, 24
Fan Status | CTFanSts | fan, run, sensor | Bool | On/Off | COV, 24
Fan VFD Speed | CTFanSpd | fan, speed, cmd | Num, 0 | % | Int, 10min
Fan VFD Freqency | CTFanVFDFreq | fan, freq, sensor | Num, 0 | Hz | Int, 10min
Pump Enabled | CTCPEnab | circ, pump, enable, cmd | Bool | Enabled/Disabled | COV, 24
Pump Command | CTCPCmd | circ, pump, run, cmd | Bool | On/Off | COV, 24
Pump Status | CTCPSts | circ, pump, run, sensor | Bool | On/Off | COV, 24
Pump VFD Speed | CTCPVFDSpd | circ, pump, speed, cmd | Num, 0 | % | Int, 10min
Pump VFD Frequency | CTCPVFDFreq | circ, pump, freq, sensor | Num, 0 | Hz | Int, 10min
Cooling Tower Blowdown Valve | CTBDVlvPos | coolingTower, water, sensor, blowdown, valve | Num, 1 | % | Int, 10min | - | New point still needs compared to Haystack
Cooling Tower Isolation Valve | CTVlvCmd | coolingTower, water, cmd, isolation, valve | Num, 1 | % | Int, 10min | - | New point still needs compared to Haystack
Cooling Water Flow | CLGWFlow | chilled, water, flow, sensor | Num, 1 | gal/min | Int, 10min | - | New point still needs compared to Haystack
Cooling Water Volume (accumulated) | CLGWVolume |  |  |  |  | - | New point still needs compared to Haystack
Cooling Water Leaving Temperature Setpoint | CLGWLTempSp | chilled, water, leaving, temp, sp | Num, 1 | F | Int, 10min | - | New point still needs compared to Haystack
Cooling Water Pressure Delta | CLGWPressDelta | chilled, water delta, pressure | Num, 1 | ∆ in w.c. | Int, 10min | - | New point still needs compared to Haystack
Cooling Water Pressure Delta Setpoint | CLGWPressDeltaSp | chiiled, water, delta, pressure, sp | Num, 1 | ∆ in w.c. | Int, 10min | - | New point still needs compared to Haystack
Cooling Tower Water Conductivity | CTWCond | coolingTower, water, conductivity | Num, 1 | ? | Int, 10min | - | New point still needs compared to Haystack
Cooling Water Static Pressure | CLGWPress |  |  |  |  | - | New point still needs compared to Haystack
Solid Separator Command | SsCmd |  |  |  |  | - | New point still needs compared to Haystack
Solid Separator Status | SsSts |  |  |  |  | - | New point still needs compared to Haystack
Energy Points - Electric |  | equip, elec, meter, coolingTower, fan [siteMeter, submeterOf]
Fan VFD Energy Total (accumulated) | CTFanVFDEnergy | fan, elec, energy, total, sensor, hisTotalized | Num, 0 | KWh | Int, 10min
Fan VFD Power Total | CTFanVFDPower | fan, elec, power, total, active, sensor | Num, 0 | kW | Int, 10min
Energy Points - Electric |  | equip, elec, meter, coolingTower, pump [siteMeter, submeterOf]
Pump VFD Energy Total (accumulated) | CTPVFDEnergy | pump, elec, energy, total, sensor, hisTotalized | Num, 0 | KWh | Int, 10min
Pump VFD Power Total | CTPVFDPower | pump, elec, power, total, active, sensor | Num, 0 | kW | Int, 10min

## HW Systems
HW Systems | Boiler | equip, boiler, hotWaterPlantRef, [condensing, automospheric] [hot water, steam] [oil, gas]
| HW System | equip, hotWaterPlant,
Description | Point Name navName | Tags | Point Type | UoM | History
Boiler Enable | BlrEnab | boiler, enable, cmd | Bool | Enabled/Disabled | COV, 24hr | enable, cmd | "boiler" is only an equip level tag in Haystack
Boiler Command | BlrCmd | boiller, run, cmd | Bool | On/Off | COV, 24hr | run, cmd | "boiler" is only an equip level tag in Haystack
Boiler Status | BlrSts | boiller, run, sensor | Bool | On/Off | COV, 24hr | run, sensor | "boiler" is only an equip level tag in Haystack
Entering Water Temperature | BlrETemp | entering, water, temp, sensor | Num, 1 | F | Int, 10min | - | -
Leaving Water Temperature | BlrLTemp | leaving, water, temp, sensor | Num, 1 | F | Int, 10min | - | -
Boiler Leaving Setpoint | BlrLTempSp | leaving, water, temp, sp | Num, 0 | F | COV, 24hr | - | -
Boiler Isolation Valve | BlrVlvCmd | isolation, valve, cmd | Bool | Open/Closed | COV, 24hr | - | -
Boiler Circulation Pump | BlrCPCmd | pump, circ, run, cmd | Bool | On/Off | COV, 24hr | - | -
Burner Level | BlrLevel | boiler, level, sensor | Num, 0 | % | Int, 10min | - | -
Boiler Firing Rate | BlrFiringRate | firingRate, sensor | Num, 1 | % | Int, 10min | - | New point still needs compared to Haystack
Boiler Run Time | BlrRuntime | runtime, sensor | Num, 1 | min | Int, 10min | - | New point still needs compared to Haystack
Systems with Heat Recovery
Heat Recovery Circulation Pump Command | HRUCPCmd | pump, circ, run, cmd | Bool | On/Off | COV, 24hr | - | -
Heat Recovery Circulation Pump Status | HRUCPSts | pump, circ, run, sensor | Bool | On/Off | COV, 24hr | - | -
Energy Points - Gas |  | equip, gas, meter, boiler
Gas Flow | BlrGasFlow | gas, flow, sensor | Num, 0 | ccf/h | Int, 10min | - | -
Gas Volume (accumulated) | BlrGasVolume | gas, volume, sensor, hisTotalized | Num, 0 | ccf | Int, 10min | - | -
Gas Energy (accumulated) | BlrGasEnergy | gas, energy, sensor, hisTotalized | Num, 0 | Mmbtu | Int, 10min | - | -
Gas Power | BlrGasPower | gas, power, sensor | Num, 0 | MMbtu/h | Int, 10min | - | -
Energy Points - Water |  | equip, water, meter, boiler
Boiler Water Temperature Entering | BlrWEtemp | water, temp, entering, sensor | Num, 1 | F | Int, 10min | - | -
Boiler Water Temperature Leaving | BlrWLTemp | water, temp, leaving, sensor | Num, 1 | F | Int, 10min | - | -
Boiler Water Flow | BlrWFlow | water, flow, sensor | Num, 1 | gal/min | Int, 10min | - | -
Boiler Water Volume (accumulated) | BlrWVolume | water, volume, hisTotalized, sensor | Num, 0 | gal | Int, 10min | - | -
Boiler Water Energy (accumulated) | BlrWEnergy | water, energy, hisTotalized, sensor | Num, 0 | MMbtu | Int, 10min | - | -
Boiler Water Power | BlrWPower | water, power, sensor | Num, 0 | MMbtu/h | Int, 10min | - | -
Energy Points - Heat Recovery Water |  | equip, water, meter, boiler, hru
Heat Recovery Water Temp Entering | HRUWEtemp | water, temp, entering, sensor | Num, 1 | F | Int, 10min |  | If these are nested underneath the boiler, you will encounter problems
Heat Recovery Water Temp Leaving | HRUWLTemp | water, temp, leaving, sensor | Num, 1 | F | Int, 10min |  | If these are nested underneath the boiler, you will encounter problems
Heat Recovery Water Flow | HRUWFlow | water, flow, sensor | Num, 0 | gal/min | Int, 10min |  | If these are nested underneath the boiler, you will encounter problems
Heat Recovery Water Volume (accumulated) | HRUWVolume | water, volume, hisTotalized, sensor | Num, 0 | gal | Int, 10min |  | If these are nested underneath the boiler, you will encounter problems
Heat Recovery Water Energy (accumulated) | HRUWEnergy | water, energy, hisTotalized, sensor | Num, 0 | MMbtu | Int, 10min |  | If these are nested underneath the boiler, you will encounter problems
Heat Recovery Water Power | HRUWPower | water, power, sensor | Num, 0 | MMbtu/h | Int, 10min |  | If these are nested underneath the boiler, you will encounter problems
HWS (Hot Water System)
Description | Point Name navName | Tags | Point Type | UoM | History | Haystack Tags | Haystack Compliance Notes
Hot Water Flow | HWFlow | hot, water, flow, sensor | Num, 1 | gal/min | Int, 10min | - | -
Hot Water Volume (accumulated) | HWVolume | hot, water, volume, sensor, hisTotalized | Num, 0 | gal | Int, 10min | - | -
Hot Water Supply Temp | HWSTemp | hot, water, leaving, temp, sensor | Num, 1 | F | COV, 15min | - | -
Hot Water Supply Temp Setpoint | HWSTempSp | hot, water, leaving, temp, sp | Num, 0 | F | COV, 24 hr | - | -
Hot Water Return Temp | HWRTemp | hot, water, entering, temp, sensor | Num, 1 | F | Int, 10min | - | -
Hot Water Pressure Delta | HWPressDelta | hot, water, pressure, delta, sensor | Num, 1 | psi | Int, 10 min | - | -
Hot Water Pressure Delta Setpoint | HWPressDeltaSp | hot, water, pressure, delta, sp | Num, 1 | psi | COV, 24 hr | - | -
Energy Points - Water |  | equip, meter, hotWaterPlant, [siteMeter, submeterOf]
Hot Water Temperature Entering | HWEtemp | hot, water, temp, entering, sensor | Num, 1 | F | Int, 10min | - | -
Hot Water Temperature Leaving | HWLTemp | hot, water, temp, leaving, sensor | Num, 1 | F | Int, 10min | - | -
Hot Water Energy (accumulated) | HWEnergy | hot, water, energy, sensor, hisTotalized | Num, 0 | MMbtu | Int, 10min | - | -
Hot Water Power | HWPower | hot, water, power, sensor | Num, 0 | MMbtu/h | Int, 10min | - | -
Building Hot Water Loop Pumps |  | equip, secondary, hot, water, pump,
Building Loop Pump Enable | HWPEnab | hot, water, pump, enable, cmd | Bool | Enabled/Disabled | COV, 24hr | - | -
Building Loop Pump Command | HWPCmd | hot, water, pump, run, cmd | Bool | On/Off | COV, 24hr | - | -
Building Loop Pump Status | HWPSts | hot, water, pump, run, sensor | Bool | On/Off | COV, 24hr | - | -
Building Loop Pump VFD Speed | HWPVFDSpd | hot, water, pump, speed, cmd | Num, 0 | % | Int, 10min | - | -
Building Loop Pump VFD Frequency | HWPVFDFreq | hot, water, pump, freq, sensor | Num, 0 | Hz | Int, 10min | - | -
Heating Water Pump Differential Pressure | HtgWPumpDiffPres | delta, hot, pressure, sensor, water | Num, 1 | ∆ in w.c. | Int, 10min | - | New point still needs compared to Haystack
Heating Water Loop Differential Pressure | HWSDiffPres | delta, hot, pressure, sensor, water | Num, 1 | ∆ in w.c. | Int, 10min | - | New point still needs compared to Haystack
Energy Points - Electric |  | equip, elec, meter, pump, hotWaterPlant, [siteMeter, submeterOf]
VFD Energy Total (accumulated) | HWPVFDEnergy | hot, water, pump, elec, energy, total, sensor, hisTotalized | Num, 0 | kWh | Int, 10min | - | -
VFD Power Total | HWPVFDPower | hot, water, pump, elec, power, total, active, sensor | Num, 0 | kW | Int, 10min | - | -

## Fan
Fans (individual) |  | equip, fan
| Discharge Fan | equip, discharge, fan
| Return Fan | equip, return, fan
| Exhaust Fan | equip, exhaust, fan
| Relief Fan | equip, relief, fan
| FCU Fan | equip, fcu, fan
| Cooling Tower | equip, coolingTower, fan
Description | Point Name navName | Tags | Point Type | UoM | History | Haystack Tags | Haystack Compliance Notes
Fan Command | FanCmd | fan, run, cmd | Bool | On/Off | COV, 24hr
Fan Status | FanSts | fan, run, sensor | Bool | On/Off | COV, 24hr | fan, run, cmd, air
Fan Speed | FanSpeed | fan, speed cmd, hisMode:cov | enum | Off/Low/Med/High | COV, 24hr | air, fan, run, sensor
Fan VFD Speed | FanVFDSpd | fan, speed, cmd | Num, 0 | % | Int, 10min | air, cmd, fan, speed hisMode:cov | This is more of a status point and should be distinguished as one
Fan VFD Frequency | FanVFDFreq | fan, freq, sensor | Num, 0 | Hz | Int, 10min | air, fan, speed, cmd
air, fan, freq, sensor
VFD Energy Total (accumulated) | VFDEnergy | fan, elec, energy, total, sensor, hisTotalized | Num, 0 | kWh | Int, 10min | - | -
VFD Power Total | VFDPower | fan, elec, power, total, active, sensor | Num, 0 | kW | Int, 10min | - | -

## Pump
Pumps (individual) |  | equip, pump
| Chiller Circ Pump | equip, pump, chiller, circ, primary
| ChW Pump | equip, pump, chilled, secondary
| Boiler Circ Pump | equip, pump, boiler, circ, primary
| HW Pump | equip, pump, hot, secondary
| DHW Pump | equip, pump, domestic, hot
| GHW Pump | equip, pump, glycol, hot
| CT Pump | equip, pump, coolingTower
| CW Pump | equip, pump, condenser
Description | Point Name navName | Tags | Point Type | UoM | History | Haystack Tags | Haystack Compliance Notes
Pump Enable | PumpEnab | pump, enable, cmd | Bool | Enabled/Disabled | COV, 24hr | - | -
Pump Command | PumpCmd | pump, run, cmd | Bool | On/Off | COV, 24hr | - | -
Pump Status | PumpSts | pump, run, sensor | Bool | On/Off | COV, 24hr | - | -
Pump VFD Speed | PumpVFDSpd | pump, speed, cmd | Num, 0 | % | Int, 10min | - | -
Pump VFD Frequency | PumpVFDFreq | pump, freq, sensor | Num, 0 | Hz | Int, 10min | - | -
Energy Points - Electric |  | equip, elec, meter, pump |  |  |  | - | -
VFD Energy Total (accumulated) | VFDEnergy | pump, elec, energy, hisTotalized, sensor | Num, 0 | kWh | Int, 10min | - | -
VFD Power Total | VFDPower | pump, elec, power, active, hisTotalized, sensor | Num, 0 | kW | Int, 10min | - | -
Energy Points - Water |  | equip, water, meter, chiller |  |  |  | equip, water, meter, pump | A BTU meter on a pump should not have the chiller tag
Water Temperature Entering | Etemp | water, temp, entering, sensor | Num, 1 | F | Int, 10min | - | -
Water Temperature Leaving | LTemp | water, temp, leaving, sensor | Num, 1 | F | Int, 10min | - | -
Water Flow | Flow | water, flow, sensor | Num, 1 | gal/min | Int, 10min | - | -
Water Volume (accumulated) | Volume | water, volume, hisTotalized, sensor | Num, 0 | gal | Int, 10min | - | -
Water Energy (accumulated) | WtrEnergy | water, energy, hisTotalized, sensor | Num, 0 | MMbtu | Int, 10min | - | -
Water Power | WtrPower | water, power, sensor | Num, 0 | MMbtu/h | Int, 10min | - | -

## Electric
Electric Meter |  | equip, elec, meter, [siteMeter, submeterOf]
Description | Point Name navName | Tags | Point Type | UoM | History | Haystack Tags | Haystack Compliance Notes
Energy Points - Electric
Energy Total (accumulated) | Energy | elec, total, energy, sensor, hisTotalized | Num, 0 | kWh | Int, 10min | - | -
Power Total | Power | elec, total, power, active, sensor | Num, 0 | kW | Int, 10min | - | -
Power Factor Total | PF | elec, total, pf, sensor | Num, 0.01unitless | unitless | Int, 10min | - | -
Power Quality Points
Current A | Current_A | elec, phase, current, sensor | Num, 1 | A | Int, 10min | - | -
Current B | Current_B | elec, phase, current, sensor | Num, 1 | A | Int, 10min | - | -
Current C | Current_C | elec, phase, current, sensor | Num, 1 | A | Int, 10min | - | -
Volts AN | Volts_AN | elec, phase, volts, sensor | Num, 0 | V | Int, 10min | - | -
Volts BN | Volts_BN | elec, phase, volts, sensor | Num, 0 | V | Int, 10min | - | -
Volts CN | Volts_CN | elec, phase, volts, sensor | Num, 0 | V | Int, 10min | - | -
Volts AB | Volts_AB | elec, phase, volts, sensor | Num, 0 | V | Int, 10min | - | -
Volts BC | Volts_BC | elec, phase, volts, sensor | Num, 0 | V | Int, 10min | - | -
Volts CA | Volts_CA | elec, phase, volts, sensor | Num, 0 | V | Int, 10min | - | -
Power Factor A | PF_A | elec, phase, pf, sensor | Num, 0.01 | unitless | Int, 10min | - | -
Power Factor B | PF_B | elec, phase, pf, sensor | Num, 0.01 | unitless | Int, 10min | - | -
Power Factor C | PF_C | elec, phase, pf, sensor | Num, 0.01 | unitless | Int, 10min | - | -
Energy A (accumulated) | Energy_A | elec, phase, energy, sensor, hisTotalized | Num, 0 | kWh | Int, 10min | - | -
Energy B (accumulated) | Energy_B | elec, phase, energy, sensor, hisTotalized | Num, 0 | kWh | Int, 10min | - | -
Energy C (accumulated) | Energy_C | elec, phase, energy, sensor, hisTotalized | Num, 0 | kWh | Int, 10min | - | -
Power A | Power_A | elec, phase, power, active, sensor | Num, 0 | kW | Int, 10min | - | -
Power B | Power_B | elec, phase, power, active, sensor | Num, 0 | kW | Int, 10min | - | -
Power C | Power_C | elec, phase, power, active, sensor | Num, 0 | kW | Int, 10min | - | -

## Gas
Gas Meter |  | equip, gas, meter, [siteMeter, submeterOf]
Description | Point Name navName | Tags | Point Type | UoM | History | Haystack Tags | Haystack Compliance Notes
Gas Flow | GasFlow | gas, flow, sensor | Num, 0 | ccf/h | Int, 10min | - | -
Gas Volume (accumulated) | GasVolume | gas, volume, sensor, hisTotalized | Num, 0 | ccf | Int, 10min | - | -
Gas Energy (accumulated) | GasEnergy | gas, energy, sensor, hisTotalized | Num, 0 | MMbtu | Int, 10min | - | -
Gas Power | GasPower | gas, power, sensor | Num, 0 | MMbtu/h | Int, 10min | - | -

## DHW
Domestic Hot Water |  | equip, domestic, hotWaterPlant
Description | Point Name navName | Tags | Point Type | UoM | History | Haystack Tags | Haystack Compliance Notes
Water Flow | DHWFlow | domestic, hot, water, flow, sensor | Num, 0 | gal/min | Int, 10min
Water Volume (accumulated) | DHWVolume | domestic, hot, water, volume, sensor, hisTotalized | Num, 0 | gal | Int, 10min
Supply Temperature | DHWSTemp | domestic, hot, water, leaving, temp, sensor | Num, 1 | F | Int, 10min
Supply Temperature Setpoint | DHWSTempSp | domestic, hot, water, leaving, temp, sp | Num, 0 | F | Int, 10min
Return Temperature | DHWRTemp | domestic, hot, water, entering, temp, sensor | Num, 1 | F | Int, 10min
DHW Building Loop Pumps |  | equip, domestic, secondary, hot, water, pump
Building Loop Pump Enable | DHWPEnab | domestic, hot, water, pump, enable, cmd | Bool | Enabled/Disabled | COV, 24hr
Building Loop Pump Command | DHWPCmd | domestic, hot, water, pump, run, cmd | Bool | On/Off | COV, 24hr
Building Loop Pump Status | DHWPSts | domestic, hot, water, pump, run, sensor | Bool | On/Off | COV, 24hr
Building Loop Pump VFD Speed | DHWPVFDSpd | domestic, hot, water, pump, speed, cmd | Num, 0 | % | Int, 10min
Building Loop Pump VFD Frequency | DHWPVFDFreq | domestic, hot, water, pump, freq, sensor | Num, 0 | Hz | Int, 10min
Heat Exchanger |  | equip, domestic, hot water, heatExchanger
DHW Heat Exchanger Enabled | HxDHWEnab | domestic, enable, cmd | Bool | Enabled/Disabled | COV, 24hr
DHW Heat Exchanger Command | HxDHWCmd | domestic, run, cmd | Bool | On/Off | COV, 24hr
DHW Heat Exchanger Runtime | HxDHWRuntime |  | Num, 1 |  | Int, 10min
DHW Water Entering Temperature | HxDHWETemp | domestic, entering, water, temp | Num, 1 | F | Int, 10min
DHW Water Leaving Temperature | HxDHWLTemp | domestic, leaving, water, temp | Num, 1 | F | Int, 10min
DHW Water Isolation Valve | HxDHWVlvCmd | domestic, isolation, valve, cmd | Bool | Open/Closed | COV, 24hr
DHW Circulation Pump Command | HxDHWCPCmd | domestic, water, circ, pump, cmd | Bool | On/Off | COV, 24hr
DHW Circulation Pump Status | HxDHWCPSts | domestic, water, circ, pump, sensor | Bool | On/Off | COV, 24hr
HWS Water Entering Temperature | HxHWSETemp | domestic, primary, entering, water, temp | Num, 1 | F | Int, 10min
HWS Water Leaving Temperature | HxHWSLTemp | domestic, primary, leaving, water, temp | Num, 1 | F | Int, 10min
HWS Water Isolation Valve | HxHWSVlvCmd | domestic, primary, isolation, valve, cmd | Bool | Open/Closed | COV, 24hr
HWS Circ Pump Command | HxHWSCPCmd | domestic, primary, water, circ, pump, cmd | Bool | On/Off | COV, 24hr
HWS Circ Pump Status | HxHWSCPSts | domestic, primary, water, circ, pump, sensor | Bool | On/Off | COV, 24hr
Energy Points - Water |  | equip, water, meter, domestic, hot
Domestic Hot Water Temperature Entering | DHWEtemp | domestic, water, temp, entering, sensor | Num, 1 | F | Int, 10min
Domestic Hot Water Temperature Leaving | DHWLTemp | domestic, water, temp, leaving, sensor | Num, 1 | F | Int, 10min
Domestic Hot Water Flow | DHWFlow | domestic, water, flow, sensor | Num, 1 | gal/min | Int, 10min
Domestic Hot Water Volume (accumulated) | DHWVolume | domestic, water, volume, sensor, hisTotalized | Num, 0 | gal | Int, 10min
Domestic Hot Water Energy (accumulated) | DHWEnergy | domestic, water, energy, sensor, hisTotalized | Num, 0 | MMbtu | Int, 10min
Domestic Hot Water Power | DHWPower | domestic, water, power, sensor | Num, 0 | MMbtu/h | Int, 10min
Energy Points - Heat Recovery Water |  | equip, water, domestic, meter, hru
Heat Recovery Water Temperature Entering | HRUWEtemp | domestic, water, temp, entering, sensor | Num, 1 | F | Int, 10min
Heat Recovery Water Temperature Leaving | HRUWLTemp | domestic, water, temp, leaving, sensor | Num, 1 | F | Int, 10min
Heat Recovery Water Flow | HRUWFlow | domestic, water, flow, sensor | Num, 1 | gal/min | Int, 10min
Heat Recovery Water Volume (accumulated) | HRUWVolume | domestic, water, volume, total, sensor | Num, 0 | gal | Int, 10min
Heat Recovery Water Energy (accumulated) | HRUWEnergy | domestic, water, energy, sensor, hisTotalized | Num, 0 | MMbtu | Int, 10min
Heat Recovery Water Power | HRUWPower | domestic, water, power, sensor | Num, 0 | MMbtu/h | Int, 10min

## EF
EF (Exhaust Fans) |  | equip, exhaust, fan
Description | Point Name navName | Tags | Point Type | UoM | History | Haystack Tags | Haystack Compliance Notes
Occupancy | Occ | occupied, cmd | Bool | Occ/UnOcc | COV, 24Hr | air, occupied,cmd
Exhaust Fan Enable | EFEnab | enable, cmd | Bool | Enabled/Disabled | COV, 24hr | air, enable, cmd
Exhaust Fan Command | EFCmd | fan, run, cmd | Bool | On/Off | COV, 24hr | air, fan, run, cmd
Exhaust Fan Status | EFSts | fan, run, sensor | Bool | On/Off | COV, 24hr | air, fan, run, sensor
Exhaust Damper Command (open/closed) | EFDmprCmd | damper, cmd | Bool | Open/Closed | COV, 24hr | air, run, fan, sensor
Exhaust Damper Position | EFDmprPos | damper, cmd | Num, 0 | % | Int, 10min | air, damper, cmd
Exhaust Damper Status | EFDmprSts | damper, sensor | Bool | On/Off | COV, 24hr | air, damper, sensor
Energy Points - Electric |  | equip, elec, meter, exhaust, fan [siteMeter, submeterOf]
VFD Energy Total (accumulated) | EFVFDEnergy | exhaust, fan, elec, energy, total, sensor, hisTotalized | Num, 0 | kWh | Int, 10min | - | -
VFD Power Total | EFVFDPower | exhaust, fan, elec, power, total, active, sensor | Num, 0 | kW | Int, 10min | - | -